## Cover Sheet
BC118 / Vertical Zero Flux Current Transformers
Technical Data Sheet Template TC010
Technical Classification:
ECCN: | N | AL: | N
These items are controlled by the U.S. Government (when labeled with “ECCN” unequal “N”) and authorized for export only to the country of ultimate destination for use by the ultimate consignee or end-user(s) herein identified. They may not be resold, transferred, or otherwise disposed of, to any other country or to any person other than the authorized ultimate consignee or end-user(s), either in their original form or after being incorporated into other items, without first obtaining approval from the U.S. Government or as otherwise authorized by U.S. law and regulations. Items labeled with "AL” unequal "N” are subject to European / national export authori-zation. Items without label or with label "AL:N" / "ECCN:N" or label”AL:9X9999” / “ECCN:9X9999”, may require authorization from responsible authorities depending on the final end-use, or the destination.
Restricted © Siemens Energy Global GmbH & Co. KG, 2021 Siemens Energy is a registered trademark licensed by Siemens AG.
Transmittal, reproduction, dissemination and/or editing of this document as well as utilization of its contents and communication thereof to others without express authorization are prohibited. Offenders will be held liable for payment of damages. All rights created by patent grant or Registration of a utility model or design patent are reserved.

## Index of Revisions
Revision Index not for the supplier - Please delete before sending to supplier!
Index of Revisions of Template
Rev. | Date | Revisions | Author | Reviewer | Approver
13 | 2021-11-24 | New template, German translations | B. Plasser |  | M. Boslau
14 | 2021-12-13 | AC accuracy description amended; DC Messfehler (german wording) | B. Plasser |  | M. Boslau

## T_C_Revision_Index_Guideline
TC Revision Index Guideline
Introduction to Guideline
This description shall be a guideline for EE and suppliers revising TC’s and assigning a practical revision numeration correctly. Problem is, that SAG and supplier use two different revision numberings for TC’s. A standard procedure guideline for revision numerating is given in this description, so that it will be easy understandable and applicable for both sides.
TC Revision Index Guideline
TC has three revision indices to manage: Rev of TC: This revision is enumerating the latest revised versions of the TC’s generated by EE. Rev of EC: This list is pursued with one higher index for each new EC version (sent to customer). Rev of Supplier: The supplier of the component has to increase the index by one for each of his new revision of the TC.
SAG-EE’s “Revision of the TC” index
An example for the top revision index list in the TC is shown in the Table 1 below. This top revision index list is designated to be filled in by SAG-EE. The TC revision index list enumeration is 0, 1, 2, ... and the correspondent TC file name P-xxxxxx_TC_AANNN_AANN_EEC010_2_S2. When the first TC version is established, the Rev of TC will be ‘0’, all by EE filled out fields shall have a white background colour (white part) and this TC is sent to supplier. The latest changes in the following TC’s, which are communicated for the first time to the supplier, have to be marked in yellow colour. Thereby, the new revision index lines and the regarding updated cells in the TC are meant. From Siemens Equipment Engineering, it is required, that updated TC’s are sent to the supplier with a higher revision index number immediately after completion. If the supplier gave information in the TC already and the component specification changed in a few points, supplier filled out cells should be kept in the latest TC document. When the component specification changes completely and a new offer is requested from the supplier, a TC with an empty and yellow marked supplier part should be given to supplier for quotation. In the right column next to the rightmost TC component specification column, information for the supplier might be offered from the EE with comments. By supplier missing or for revision required values should be highlighted with red coloured comments in this comment column.
P-xxxxxx_TC_AANNN_AANN_EEC010_3_S2_commented
Revisions
Rev of TC | Remarks | Date | by | Rev of EC
0 | First Issue | 2016-01-14 | AF | 00
1 | Wording in line 1.3 to 1.6 changed | 2016-01-29 | AF | -
2 | Changes acc. to agreement with System Design | 2016-02-26 | AF | 01
3 | Update acc. to Customer comments | 2016-04-19 | AF | 02
Table 1: Top revision index “Rev of TC” for the document P-xxxxxx_TC_AANNN_AANN_EEC010_3_S2_commented
TC’s “Rev of Supplier” Index
The bottom “Rev of Supplier” index list in the light yellow part of TC is designated to be filled in by the suppliers. Supplier revision index numeration is S0, S1, S2, ... . S stands for supplier. So the supplier will also have a revision index list. To the TC excel file name, this index is appended as well after EE revision index, i.e. as P-xxxxxx_TC_AANNN_AANN_EEC010_2_S2_commented. The supplier has to fill out the revision index list with information about the latest changes. The manufacturer also marks changes clearly in TC for example by marking cells with yellow colour. Table 2 shows the bottom “Rev of Supplier” list, which is filled out by the supplier:
P-xxxxxx_TC_AANNN_AANN_EEC010_4_S2_commented
Rev of Supplier | Remarks | Date | by
S0 | First Design | 2016-01-28 | DU
S1 | Update acc. Rev 3 of TC / Rev B of EC | 2016-04-29 | DU
S2 | Update acc. Comments from EE | 2016-05-09 | DU
Table 2: Supplier revision index “Rev of TC” for the document P-xxxxxx_TC_AANNN_AANN_EEC010_4_S2_commented
Typical and Possible TC revisions as example
The following Table 3 shows a typical history of TC document names; the revisions inside the document have to be the same:
TC document name
P-xxxxxx_TC_AANNN_AANN_EEC010_0
P-xxxxxx_TC_AANNN_AANN_EEC010_0_S0
P-xxxxxx_TC_AANNN_AANN_EEC010_0_S0_commented
P-xxxxxx_TC_AANNN_AANN_EEC010_0_S1
P-xxxxxx_TC_AANNN_AANN_EEC010_0_S1_commented
P-xxxxxx_TC_AANNN_AANN_EEC010_0_S2
P-xxxxxx_TC_AANNN_AANN_EEC010_1_S2_commented
P-xxxxxx_TC_AANNN_AANN_EEC010_1_S3
P-xxxxxx_TC_AANNN_AANN_EEC010_1_S3_commented
P-xxxxxx_TC_AANNN_AANN_EEC010_1_S4
P-xxxxxx_TC_AANNN_AANN_EEC010_1_S4_final
Table 3: TC document name history
Prevention of TC update conflicts between EE and suppliers
When a TC update is being sent to the supplier, it could arise that the TC is updated by the supplier parallel to current working from EE on the latest TC version. For that reason it is very important to act according to "the ball is in your court" principle. This means via communication it has to be clear who (EE or Supplier) is working on the TC. Parallel actions have to be avoided.

## TC010_BC118
|  |  | 12 | Revisions |  | 12 | Revisionen
|  |  | Index | Remarks |  | Index | Beschreibung | Datum | by | Rev. / date of EEC010 | Rev. / date of Study Report
|  |  | 0 | First Issue |  | 0 |  | 2022-08-25 | JH |  | 220727_2GW-C_PRELIM_VCR_v01
|  |  | 1 | Changes Marked red, Power Supply Voltage, Transient Plots |  | 1 |  | 2022-10-05 | JH |  | 220727_2GW-C_PRELIM_VCR_v01
|  |  | 2 | Changes Marked grey, New VZF necessary |  | 2 |  | 2022-10-14 | JH |  | 220727_2GW-C_PRELIM_VCR_v01
Compl. TD3 | only for ED3
|  | Doc. Ref.: |  | I-U81102_TC_BC118_AANN_EEC010 | [5 empty] | Project Name: 2GW-C
|  | Project: |  | 2GW-C
|  | Doc. Title: |  | Technical data sheet, Freestanding Zero Flux Current Transformers
x | x | English | Converter Stations |  | Deutsch |  |  |  | Offshore | Onshore
x | x |  | Location designation |  |  | Anlagenortskennzeichen nach SLD |  |  | CV11-TD10-TB01-BC01 CV11-TD20-TB01-BC01 | CV12-TD10-TB01-BC01 CV12-TD20-TB01-BC01
x | x |  | Items |  |  | Gerät |  | units | CV11_M_01 CV11_S_01 | CV12_M_01 CV12_M_01
x |  |  | Modularization Number | Basic Type |  | Modularisierungs-No.: | Grundtyp | -
x |  |  |  | Type Description |  |  | Typbeschreibung | -
x |  |  | Supplier | Offer Number |  | Hersteller | Angebotsnummer | -
x |  |  |  | Offer Item |  |  | Angebotsposition | -
x |  |  |  | Offer Date |  |  | Angebotsdatum | -
x | x |  | Main Data |  |  | Hauptdaten
x | x |  | Measuring principle |  |  | Messprinzip |  | - | zero flux compensation | zero flux compensation
x | x |  | Type of insulator (composite only) |  |  | Isolatortyp |  | - | composite | composite
x | x |  | Type of insulation (SF6 only) |  |  | Isolationsart |  | - | SF6 | SF6
x | x |  | Insulation Location according to Insulation Coordination |  |  | Isolationspunkt gemäß "Isolationskoordination" |  | - | S | S
x | x |  | Installation location | indoor / outdoor |  | Ausführungsart | Innenbereich / Freiluft | - | indoor | indoor
x |  |  | Application (IC, ICP, ICN, IdLH, IdCN, IdLN, IdEE, IdLHG , IdSG) |  |  | Anwendung (IC, ICP, ICN, IdLH, IdCN, IdLN, IdEE, IdLHG, IdSG) |  | - | IC | IC
x | x |  | Type of Measuring Head (normal / more iron) |  |  | Typ des Messkopfs (Normal / Erhöhter Eisenanteil) |  | - | H067B- extra iron | H067B - extra iron
x | x |  | Core quantity |  |  | Anzahl der Messköpfe |  | pcs | 2 | 2
x | x |  | Type of Electronics Module (HITACC: HCv / FLv / SLv) |  |  | Typ des Elektronikmoduls (HITACC: HCv / FLv / SLv; CURACC) |  | - | HITACC SLv | HITACC SLv
x | x |  | Type of signal | output 1 |  | Signaltyp | Ausgang 1 | - | High Bandwidth (HB) | High Bandwidth (HB)
x | x |  |  | output 2 |  |  | Ausgang 2 | - | lowpass (NB) | lowpass (NB)
x | x |  | Electrical data |  |  | Elektrische Daten |  | -
x | x |  | MCOV Maximum Continuous Operating Voltage (line to ground) |  |  | Maximale Dauerbetriebsspannung AC (MCOV) |  | kVrms | 204 | 196
x | x |  | DCOV (highest DC voltage for equipment) |  |  | Maximale Dauerbetriebsspannung DC (DCOV) |  | kV | 275 | 275
x | x |  | CCOV Crest value of Continuous Operating Voltage (highest mixed AC / DC voltage for equipment, superposition) |  |  | Maximale Scheitelspannung (CCOV) |  | kV | 531 | 526
x | x |  | BVCC Base Voltage for Creepage Calculation (line to ground) |  |  | Spannung zur Kriechwegsberechnung (BVCC) |  | kV | 397 | 389
x | x |  | Rated frequency fr |  |  | Nennfrequenz |  | Hz | 50 | 50
x |  |  | Rated short-time thermal current (Ith) |  |  | Thermischer Bemessungskurzschlussstrom (Ith) |  | kArms | 6.3 | 12.5
x | x |  | LIWV (Lightning impulse withstand voltage) |  |  | Blitzstoßspannungspegel | Leiter - Erde | kVpeak | 1139 | 1362
x | x |  | SIWV (Switching impulse withstand voltage) |  |  | Schaltstoßspannungspegel | Leiter - Erde | kVpeak | 1002 | 1002
x |  |  | DC voltage withstand test level (60 min) |  |  | DC Stehspannung Prüfpegel (60min) |  | kVdc | 777.9 | 763.2
x |  |  | PFWV (Power frequency withstand voltage) |  |  | Wechselspannungsprüfpegel |  | kVRMS | 593.0584 | 580.934
x | x |  | Minimum creepage distance |  |  | Minimaler Kriechweg |  | - | - | -
x | x |  | Note: Diameter correction acc. to General Data | specific (line to ground) |  | Bemerkung: Durchmesser- korrektur gemäß General Data | spezifisch (Leiter gegen Erde) | mm/kV | 20 | 20
x | x |  |  | absolute |  |  | absolut | mm | 7940 | 7780
x |  |  | Requirements for DC & Mixed Voltage Outdoor Insulator Shed Profiles (as per IEC 60815-4) |  |  | Anforderungen an DC und Mischspannungsbelasteten Isolatorprofilen für Freiluftaufstellung (gemäß IEC 60815-4)
x |  |  | Creepage factor CF (l/s) | Porcelain (non-HTM) |  | Kriechwegsfaktor CF (l/s) | Porzellan (non-HTM) |  | ≤ 3.5 | ≤ 3.5
x |  |  |  | Composite / Hybrid (HTM) |  |  | Verbundstoff / Hybrid (HTM) |  | ≤ 4.2 | ≤ 4.2
x |  |  | Spacing versus shed overhang (S/P) | Porcelain / (non-HTM) |  | Verhältnis Schrimabstand zu Schirmüberhang (S/P) | Porzellan (non-HTM) |  | ≥ 1 | ≥ 1
x |  |  |  | Composite / Hybrid (HTM) |  |  | Verbundstoff / Hybrid (HTM) |  | ≥ 0,9 | ≥ 0,9
x |  |  | Requirements for AC Voltage Indoor/Outdoor and DC Voltage Indoor Insulator Shed Profiles (as per IEC 60815-2/3) |  |  | Anforderungen an AC belastete (Innenraum- / Freiluftaufstellung) und DC belastete (Innenraum) Isolatorprofile (gemäß IEC 60815-2/3)
x | x |  | Max. RIV level at 1.1*Um /Ö3 | (line to ground) |  | Max. RIV Level bei 1.1*Um /Ö3 | (Leiter gegen Erde) | µV at 1 MHz | <2500 | <2500
x | x |  | Nominal current (1 p.u.) of output 1 |  |  | Nennstrom (1 p.u.) von Ausgang 1 |  | A | ±3000 | ±3000
x | x |  | Current measuring range (2 p.u.) of output 1 |  |  | Strommessbereich (2 p.u.) von Ausgang 1 |  | A | ±6000 | ±6000
x |  |  | Current measuring range of output 2 |  |  | Strommessbereich von Ausgang 2 |  | A | ±100 | ±100
x |  |  | Max. overload current |  |  | Max. Überlaststrom |  | kA | 30 | 30
x |  |  | No saturation of head |  |  | Keine Sättigung des Messkopfs |  | ms | >30 | >30
x |  |  | Maximum overload current without saturation of the measuring head |  |  | Maximaler Überstrom ohne Sättigung des Messkopfs |  | - | check and refer to tab: transient plots | check and refer to tab: transient plots
x | x |  | Measuring system data |  |  | Messsystem Daten |  | -
x | x |  | Output 1: Transfer ratio |  |  | Ausgang 1: Übertragungsverhältnis |  | - | ±10 V @ ±6000 A | ±10 V @ ±6000 A
x | x |  | Output 2: Transfer ratio |  |  | Ausgang 2: Übertragungsverhältnis |  | - | ± 10 V @ ± 100 ADC | ± 10 V @ ± 100 ADC
x |  |  | Output load, range 0…12 Ω (only for current output) |  |  | Impedanz am Stromausgang (zwischen 0…12 Ω) |  | Ohm | -
x |  |  | Impedance on voltage output (at least 1k ohm) |  |  | Impedanz am Spannungsausgang (mindestens 1 kΩ) |  | kOhm | >1 | >1
x | x |  | Dynamic response (measuring system) |  |  | Dynamisches Verhalten (Messsystem) |  | - | - | -
x | x |  | Output 1: |  |  | Ausgang 1: |  | - | - | -
x | x |  | Bandwidth (-3dB Amplitude IPr to Imeas) refer to note 1*) |  |  | Bandbreite (-3dB Amplitude IPr zu Imeas) siehe Anmerkung 1*) |  | kHz | >10 | >10
x |  |  | Bandwidth (-3dB Amplitude IPr to Imeas) refer to note 1*) (Manufacturer) |  |  | Bandbreite (-3dB Amplitude IPr zu Imeas) siehe Anmerkung 1*) (Hersteller) |  | kHz | >20 | >20
x | x |  | Tracking delay time (Dead time) |  |  | Verzögerungszeit (Totzeit) |  | µs | <5 | <5
x | x |  | Minimum slew rate |  |  | minimale Anstiegsgeschwindigkeit |  | A / µs | >15 | >15
x |  |  | Minimum slew rate (Manufacturer) |  |  | minimale Anstiegsgeschwindigkeit (Hersteller) |  | A / µs | > 30 | > 30
x | x |  | Output 2: |  |  | Ausgang 2: |  | - | -
x | x |  | Bandwidth (-3dB) |  |  | Bandbreite (-3dB) |  | kHz | DC...0.008 | DC...0.008
x | x |  | Accuracy (Measuring System) |  |  | Genauigkeit (des Messsystems) |  | -
x | x |  | Output 1 |  |  | Ausgang 1: |  | - | - | -
x | x |  | 1) DC offset referring to current measuring range |  |  | 1) DC Offset bezogen auf den Strommessbereich |  | % | 0.02 | 0.02
x | x |  | 2) DC accuracy of reading (of measured value) |  |  | 2) DC Messfehler (vom Messwert) |  | % | <=0,1 | 0.1
x | x |  | Total DC accuracy |  |  | Gesamte DC Genauigkeit |  | % | Amplitude resulting from 1) plus 2) | Amplitude resulting from 1) plus 2)
x | x |  | 3) Output noise (peak to peak) referring to nominal current |  |  | 3) Ausgangsrauschen (Spitze-Spitze) bezogen auf den Nennstrom |  | % | 0.1 | 0.1
x | x |  | 4) AC amplitude error (frequency related accuracy) |  |  | 4) AC Amplitudenfehler (frequenzbezogene Genauigkeit) |  | % | 0.2 x f[kHz]^2 | 0.2 x f[kHz]^2
x | x |  | Total AC accuracy |  |  | Gesamte AC Genauigkeit |  | A | Amplitude resulting from 3) plus 4) | Amplitude resulting from 3) plus 4)
x | x |  | Output 2 |  |  | Ausgang 2: |  | - | - | -
x | x |  | Permissible absolute error of output 2 / DC loupe |  |  | Zulässiger absoluter Fehler der DC Lupe / Ausgang 2 |  | % | 0.2 | 0.2
x |  |  | Permissible absolute error of output 2 / DC loupe (Manufacturer) |  |  | Zulässiger absoluter Fehler der DC Lupe / Ausgang 2 (Hersteller) |  | % | 0.2 | 0.2
x | x |  | Power supply (Electronics Module) |  |  | Stromversorgung (Elektronikmodul) |  | - | - | -
x | x |  | Nominal voltage; (110VDC or 220VDC) |  |  | Nennspannung; (110VDC oder 220VDC) |  | Vdc | 220 | 220
x | x |  | Tolerance of voltage, minimum |  |  | Spannungstoleranz, Minimum |  | % | -15 | -15
x | x |  | Tolerance of voltage, maximum |  |  | Spannungstoleranz, Maximum |  | % | 20 | 20
x | x |  | Mechanical data |  |  | Mechanische Daten |  | -
x | x |  | Interface at Electronics Module (Harting plug ) |  |  | Schnittstellen am Elektronikmodul |  | - | Harting plug | Harting plug
x | x |  | Interface at Terminal Box at VZF (Harting plug) |  |  | Schnittstelle am Messkopf |  | - | Harting plug | Harting plug
x | x |  | Required length of interconnection cables |  |  | Erforderliche Länge der Verbindungskabel |  | m | <300 | <300
x | x |  | Interconnection cable type |  |  | Verbindungskabeltyp |  | - | twisted & screened pairs + overall screen | twisted & screened pairs + overall screen
x |  |  | Terminal forces, static |  |  | Maximal zulässige Kräfte an Primäranschlüssen, statisch |  | kN | 2 | 2
x |  |  | Terminal forces, dynamic |  |  | Maximal zulässige Kräfte an Primäranschlüssen, dynamisch |  | kN | 5 | 5
x |  |  | On-site testing of the gas-density meter without deinstallation (e.g.WIKA Valve Testing Device) |  |  | Vorortprüfung des Gasdichtewächtes ohne Demontage möglich |  | - | yes | yes
x |  |  | Project related data |  |  | Projektspezifische Daten |  | -
x |  |  | Maintenance intervall |  |  | Wartungsintervall |  | months | 24 | 24
x |  |  | Minimum ambient temperature |  |  | Minimale Umgebungstemperatur |  | °C | please refer to General Data | please refer to General Data
x |  |  | Maximum ambient temperature |  |  | Maximale Umgebungstemperatur |  | °C | please refer to General Data | please refer to General Data
x |  |  | Quantities |  |  | Stückzahlen |  | - |  | -
x |  |  | main | Measuring Heads+housing |  | Hauptlieferung | Messköpfe+Gehäuse | pcs | 6 | 6
x |  |  |  | Electronics Module |  |  | Elektronikmodule | pcs | 12 | 12
x |  |  | spare | Measuring Heads+housing |  | Ersatzteile | Messköpfe+Gehäuse | pcs | 1 | 1
x |  |  |  | Electronics Module |  |  | Elektronikmodule | pcs | 2 | 2
x |  |  | Head shorting plug (at Measuring Head) | for system HITACC only |  | Kurzschlussstecker (Messkopf) | nur für HITACC | pcs | - | -
x |  |  | Short ciruit socket (for EM exchange) | for system HITACC only |  | Kurzschlussbuchse (für EM Tausch) | nur für HITACC | pcs | - | -
x | x |  | Note 1*) IPr 100% Amplitude for 0…500 Hz; De-rate IPr inversely proportional to 5% at 10 kHz and higher |  |  | Anmerkung 1*) IPr 100% Amplitude für 0…500 Hz; Herabstufung von IPr, umgekehrt proportional zu 5% bei 10 kHz und höher
Part of subcontractor - please fill in in the yellow marked cells
|  |  | Rev | Remarks |  |  |  | Date |  |  | by
0
1
2
3
|  |  | #REF! |  |  | #REF! |  |  |  |  | legend: | please fill in the yellow marked cells | please fill in the yellow marked cells
|  |  | Part for subcontractor |  |  | Part for subcontractor | [5 empty] | white cells contain requirements | white cells contain requirements
|  |  | - please fill out - |  |  | - please fill out - |  |  |  |  | offered | offered | offered
|  |  | Manufacturer type identification |  |  | Manufacturer type identification
|  |  | Outline drawing no. |  |  | Outline drawing no.
|  |  | Manufacturer |  |  | Manufacturer
|  |  | Type |  |  | Type
|  |  | Main Data |  |  | Main Data
|  |  | MTBF/ MTTF |  |  | MTBF/ MTTF |  | h
|  |  | tcorr (Fault correction or restoration time) | incl. time required for related work on the concerned component or on neightboring equipment |  | tcorr (Fault correction or restoration time) | incl. time required for related work on the concerned component or on neightboring equipment | h
|  |  | ttest (Time for adjustment, setting, checking and testing of repaired or replaced equipment) |  |  | ttest (Time for adjustment, setting, checking and testing of repaired or replaced equipment) |  | h
|  |  | Gas for first filling included |  |  | Gas for first filling included |  | yes/no
|  |  | Primary Circuit |  |  | Primary Circuit
|  |  | Nominal current (1 p.u.) |  |  | Nominal current (1 p.u.) |  | A
|  |  | Output current range (2 p.u.) |  |  | Output current range (2 p.u.) |  | A
|  |  | Short circuit current (0.5 s), internally saturation free |  |  | Short circuit current (0.5 s), internally saturation free |  | kA
|  |  | Output Circuit |  |  | Output Circuit
|  |  | Output 1: Transfer ratio |  |  | Output 1: Transfer ratio
|  |  | Output 2: Transfer ratio |  |  | Output 2: Transfer ratio
|  |  | Internal impedance |  |  | Internal impedance |  | Ω
|  |  | Dynamic response |  |  | Dynamic response
|  |  | Output 1: |  |  | Output 1:
|  |  | Operating frequency |  |  | Operating frequency |  | kHz
|  |  | Bandwidth less than 10% of nominal current |  |  | Bandwidth less than 10% of nominal current |  | kHz
|  |  | Limiting frequency |  |  | Limiting frequency |  | kHz
|  |  | Step response time (from 0.1 p.u - 0.9 p.u.) |  |  | Step response time (from 0.1 p.u - 0.9 p.u.) |  | µs
|  |  | Slewing rate (primary / secondary) |  |  | Slewing rate (primary / secondary)
|  |  | Output 2: |  |  | Output 2:
|  |  | Bandwidth |  |  | Bandwidth
|  |  | Tracking error (Step response, ±1p.u. step) |  |  | Tracking error (Step response, ±1p.u. step)
|  |  | rise / fall time |  |  | rise / fall time |  | A / µs
|  |  | settling time (error within 1% of 1 p.u.) |  |  | settling time (error within 1% of 1 p.u.) |  | µs
|  |  | Accuracy |  |  | Accuracy
|  |  | output 1 |  |  | output 1 |  | %
|  |  | output 2 (slow signal resolution) |  |  | output 2 (slow signal resolution) |  | %
|  |  | DC-accuracy of output 1 (Ip 0…1pu) |  |  | DC-accuracy of output 1 (Ip 0…1pu)
|  |  | DC-accuracy of output 2 (Ip 0…50A DC superimposed with 1500 Amps rms AC) |  |  | DC-accuracy of output 2 (Ip 0…50A DC superimposed with 1500 Amps rms AC)
|  |  | AC-accuracy of output 1 (sinusoidal current) |  |  | AC-accuracy of output 1 (sinusoidal current)
|  |  | Electronics, temperature range inside cubicle |  |  | Electronics, temperature range inside cubicle
|  |  | Max. operating temp. (reduced accuracy) |  |  | Max. operating temp. (reduced accuracy) |  | °C
|  |  | di / dt to be accurately followed in case of transients |  |  | di / dt to be accurately followed in case of transients
|  |  | Power supply |  |  | Power supply
|  |  | Nominal voltage |  |  | Nominal voltage |  | V DC
|  |  | Tolerance of voltage |  |  | Tolerance of voltage |  | %
|  |  | Power consumption at Ip=0 |  |  | Power consumption at Ip=0 |  | W
|  |  | Power consumption at Ip=6kA |  |  | Power consumption at Ip=6kA |  | W
|  |  | Electrical data |  |  | Electrical data
|  |  | Insulation electronics module |  |  | Insulation electronics module |  | kV AC
|  |  | Mechanical data (VZF) |  |  | Mechanical data (VZF)
|  |  | Total weight |  |  | Total weight |  | kg
|  |  | Total height |  |  | Total height |  | mm
|  |  | Total width |  |  | Total width |  | mm
|  |  | Total depth |  |  | Total depth |  | mm
|  |  | colour of insulator |  |  | colour of insulator
|  |  | LIWL |  |  | LIWL |  | kVpk
|  |  | SIWL |  |  | SIWL |  | kVpk
|  |  | PFWL |  |  | PFWL |  | kV
|  |  | Average diameter Da of insulator |  |  | Average diameter Da of insulator |  | mm
|  |  | Mechanical terminal load in all direction |  |  | Mechanical terminal load in all direction
|  |  |  | Static |  |  | Static | kN
|  |  |  | Dynamic |  |  | Dynamic | kN
|  |  | Terminal force | Static |  | Terminal force | Static | kN
|  |  | Terminal force | Dynamic |  | Terminal force | Dynamic | kN
|  |  | Terminal Standard | HV |  | Terminal Standard | HV
|  |  |  | LV |  |  | LV
|  |  |  | Gr |  |  | Gr
|  |  | installation site | (outdoor, indoor) |  | installation site | (outdoor, indoor)
|  |  | Ambient air Temperature range |  |  | Ambient air Temperature range
|  |  |  | min. |  |  | min. | °C
|  |  |  | max. |  |  | max. | °C
|  |  | Altitude above sea level |  |  | Altitude above sea level |  | m
|  |  | Wind velocity |  |  | Wind velocity |  | m/s
|  |  | Wind pressure |  |  | Wind pressure |  | kN/m2
|  |  | Ice coating |  |  | Ice coating |  | mm
|  |  | Acceleration in centre of gravity |  |  | Acceleration in centre of gravity
|  |  |  | horizontal |  |  | horizontal | g
|  |  |  | vertical |  |  | vertical | g
|  |  | On-site testing of the gas-density meter without deinstallation (e.g.WIKA Valve Testing Device) |  |  | On-site testing of the gas-density meter without deinstallation (e.g.WIKA Valve Testing Device) |  | -
|  |  | Interconnection cable type |  |  | Interconnection cable type
|  |  | Type Tests |  |  | Type Tests
|  |  | Temperature rise test (IEC 61869-1) |  |  | Temperature rise test (IEC 61869-1) |  | EUR
|  |  |  | existing |  |  | existing | yes/no
|  |  | Lightning impulse voltage test (IEC 61869-1) |  |  | Lightning impulse voltage test (IEC 61869-1) |  | EUR
|  |  |  | existing |  |  | existing | yes/no
|  |  | Switching impulse voltage test (IEC 61869-1) |  |  | Switching impulse voltage test (IEC 61869-1) |  | EUR
|  |  |  | existing |  |  | existing | yes/no
|  |  | Wet test for outdoor type transformers (IEC 61869-1) |  |  | Wet test for outdoor type transformers (IEC 61869-1) |  | EUR
|  |  |  | existing |  |  | existing | yes/no
|  |  | EMC Test (IEC 61869-1) |  |  | EMC Test (IEC 61869-1) |  | EUR
|  |  | RIV Test | existing |  | RIV Test | existing | yes/no
|  |  | Tests for accuracy (IEC 61869-1) |  |  | Tests for accuracy (IEC 61869-1) |  | EUR
|  |  |  | existing |  |  | existing | yes/no
|  |  | Verification of drgree of protection by enclosures (IEC 61869-1) |  |  | Verification of drgree of protection by enclosures (IEC 61869-1) |  | EUR
|  |  |  | existing |  |  | existing | yes/no
|  |  | Enclosure tightness test at ambient temperature (IEC 61869-1) |  |  | Enclosure tightness test at ambient temperature (IEC 61869-1) |  | EUR
|  |  |  | existing |  |  | existing | yes/no
|  |  | Pressure test for the enclosure (IEC 61869-1) |  |  | Pressure test for the enclosure (IEC 61869-1) |  | EUR
|  |  |  | existing |  |  | existing | yes/no
|  |  | Frequency response (acc. Manufacturer) |  |  | Frequency response (acc. Manufacturer) |  | EUR | [5 empty] | Type tests nach IEC 61869-1 und IEC 61869-2
|  |  |  | existing |  |  | existing | yes/no
|  |  | Short time current test (IEC 61869-2) |  |  | Short time current test (IEC 61869-2) |  | EUR | [5 empty] | OK 61869-1 | Temperature rise test
|  |  |  | existing |  |  | existing | yes/no | [5 empty] | OK 61869-1 | Lightning Impulse voltage test
|  |  | Environmental testing (IEC 60068-2-2 Test Bd) |  |  | Environmental testing (IEC 60068-2-2 Test Bd) |  | EUR | [5 empty] | OK 61869-1 | Switching Impulse voltage test
|  |  | Dry heat test | existing |  | Dry heat test | existing | yes/no | [5 empty] | OK 61869-1 | Wet test for outdoor type transformers
|  |  | Environmental testing (IEC 60068-2-78) |  |  | Environmental testing (IEC 60068-2-78) |  | EUR | [5 empty] | OK 61869-1 | Electromagnetic Compatibility tests (contains RIV test)
|  |  | Damp heat test | existing |  | Damp heat test | existing | yes/no | [5 empty] | OK 61869-1 | Tests for accuracy
|  |  | EMC test (IEC 61000-4-2) |  |  | EMC test (IEC 61000-4-2) |  | EUR | [5 empty] | OK 61869-1 | Verification of degree of protection by enclosures
|  |  | Electro-static discharge test | existing |  | Electro-static discharge test | existing | yes/no | [5 empty] | OK 61869-1 | Enclosure tightness test at ambient temperature
|  |  | EMC test (IEC 60255-22-1 & IEC61000-4-18) |  |  | EMC test (IEC 60255-22-1 & IEC61000-4-18) |  | EUR | [5 empty] | OK 61869-1 | Pressure test for the enclosure
|  |  | Damped oscillatory wave immunity test | existing |  | Damped oscillatory wave immunity test | existing | yes/no | [5 empty] | OK 61869-2 | Short time current test
|  |  | Impulse voltage withstand test (IEC 60255-5) |  |  | Impulse voltage withstand test (IEC 60255-5) |  | EUR
|  |  |  | existing |  |  | existing | yes/no
|  |  | Power supply inrush current (acc. Manufacturer) |  |  | Power supply inrush current (acc. Manufacturer) |  | EUR
|  |  |  | existing |  |  | existing | yes/no
|  |  | Step response (acc. Manufacturer) |  |  | Step response (acc. Manufacturer) |  | EUR
|  |  |  | existing |  |  | existing | yes/no
|  |  | Routine Tests |  |  | Routine Tests |  | incl.
|  |  | VZF |  |  | VZF
|  |  | Power frequency withstand test on primary terminals (IEC 61869-1) |  |  | Power frequency withstand test on primary terminals (IEC 61869-1) |  | yes/no | [5 empty] | Routine tests nach IEC 61869-1 und IEC 61869-2
|  |  | Partial discharge measurement (IEC 61869-1) |  |  | Partial discharge measurement (IEC 61869-1) |  | yes/no
|  |  | Power frequency withstand tests between sections (IEC 61869-1) |  |  | Power frequency withstand tests between sections (IEC 61869-1) |  | yes/no | [5 empty] | OK 61869-1 | Power frequency withstand test on primary terminals
|  |  | Power frequency withstand test on secondary terminals (IEC 61869-1) |  |  | Power frequency withstand test on secondary terminals (IEC 61869-1) |  | yes/no | [5 empty] | OK 61869-1 | Partial discharge measurement
|  |  | Tests for accuracy (IEC 61869-1) |  |  | Tests for accuracy (IEC 61869-1) |  | yes/no | [5 empty] | OK 61869-1 | Power frequency withstand tests between sections
|  |  | Verification of terminal markings (IEC 61869-1) |  |  | Verification of terminal markings (IEC 61869-1) |  | yes/no | [5 empty] | OK 61869-1 | Power frequency withstand test on secondary terminals
|  |  | Enclosure tightness test at ambient temperature (IEC 61869-1) |  |  | Enclosure tightness test at ambient temperature (IEC 61869-1) |  | yes/no | [5 empty] | OK 61869-1 | Test for accuracy
|  |  | Pressure test for the enclosure (IEC 61869-1) |  |  | Pressure test for the enclosure (IEC 61869-1) |  | yes/no | [5 empty] | OK 61869-1 | Verification of terminal markings
|  |  | inter-turn overvoltage test IEC 61869-2) |  |  | inter-turn overvoltage test IEC 61869-2) |  | yes/no | [5 empty] | OK 61869-1 | Enclosure tightness test at ambient temperature
|  |  | 1 Electronics Module |  |  | 1 Electronics Module | [7 empty] | OK 61869-1 | Pressure test for the enclosure
|  |  | 1A Visual inspection |  |  | 1A Visual inspection |  | yes/no | [5 empty] | OK 61869-2 | inter-turn overvoltage test
|  |  | 1B Power frequency voltage withstand, 1 min. |  |  | 1B Power frequency voltage withstand, 1 min. |  | yes/no
|  |  | 1C Insulation resistance: |  |  | 1C Insulation resistance:
|  |  | - all terminals to ground |  |  | - all terminals to ground |  | yes/no
|  |  | - supply terminals to other terminals and ground |  |  | - supply terminals to other terminals and ground |  | yes/no
|  |  | 1D Power supply check |  |  | 1D Power supply check |  | yes/no
|  |  | 2 Measuring head, before encapsulation |  |  | 2 Measuring head, before encapsulation
|  |  | (high current type only) |  |  | (high current type only)
|  |  | 2A Visual inspection |  |  | 2A Visual inspection |  | yes/no
|  |  | 2B Power frequency voltage withstand, 1 min. on secondary terminals |  |  | 2B Power frequency voltage withstand, 1 min. on secondary terminals |  | yes/no
|  |  | 2C Inter-turn overvoltage test |  |  | 2C Inter-turn overvoltage test |  | yes/no
|  |  | 2D Insulation resistance test |  |  | 2D Insulation resistance test |  | yes/no
|  |  | 2E Winding resistance (FLC20 after encapsulation) |  |  | 2E Winding resistance (FLC20 after encapsulation) |  | yes/no
|  |  | 2F Ratio test (FLC20 after encapsulation) |  |  | 2F Ratio test (FLC20 after encapsulation) |  | yes/no
|  |  | 2G Induced voltage |  |  | 2G Induced voltage |  | yes/no
|  |  | 3 Measuring head, after encapsulation |  |  | 3 Measuring head, after encapsulation
|  |  | 3A Visual inspaction |  |  | 3A Visual inspaction
|  |  | 3B Power frequency voltage withstand test, 1 min. on secondary terminals |  |  | 3B Power frequency voltage withstand test, 1 min. on secondary terminals |  | yes/no
|  |  | 3C Insulation resistance test |  |  | 3C Insulation resistance test |  | yes/no
|  |  | 3D Polarity check |  |  | 3D Polarity check |  | yes/no
|  |  | 3E Induced voltage |  |  | 3E Induced voltage |  | yes/no
|  |  | 4 Electronics Module + Mesuring head |  |  | 4 Electronics Module + Mesuring head
|  |  | 4A Visual inspection |  |  | 4A Visual inspection |  | yes/no
|  |  | 4B Polarity check |  |  | 4B Polarity check |  | yes/no
|  |  | 4C DC accuracy test and linearity (Output 1) |  |  | 4C DC accuracy test and linearity (Output 1) |  | yes/no
|  |  | 4D Ripple of output signal |  |  | 4D Ripple of output signal |  | yes/no
|  |  | 4E DC accuracy test and llinearity (Output 2, only FLC6000) |  |  | 4E DC accuracy test and llinearity (Output 2, only FLC6000) |  | yes/no
|  |  | 4F Induced voltage |  |  | 4F Induced voltage |  | yes/no

## Transient Plots
Offshore:
Location:
S
¦Imax¦ = 14,6 kA
Onshore:
Location:
S
¦Imax¦ = 33,2 kA

## Overview Types of Electronics
=== Confidential ==== for internal use only; please delete this tab before sending external
Overview of Electronic Modules for Halfbridge Configurations:
Thermischer Bemessungskurzschlussstrom (Ith)
|  | DC Überlagerte Blitzstoßspannung | Leiter - Erde
Leiter - Erde
|  | DC Überlagerte Schaltstoßspannung | Leiter - Erde
Leiter - Erde
| Minimum creepage distance | Minimaler Kriechweg
Anforderungen an AC belastete (Innenraum- / Freiluftaufstellung) und DC belastete (Innenraum) Isolatorprofile (gemäß IEC 60815-2/3)
Nennstrom (1 p.u.) von Ausgang 1
Strommessbereich (2 p.u.) von Ausgang 1
Strommessbereich von Ausgang 2
Max. Überlaststrom
Keine Sättigung des Messkopfs
Type des Messkopfes
Anzahl der Messköpfe
Messsystem Daten
Elektronikmodul Typ
Ausgang 1: Übertragungsverhältnis
Ausgang 2: Übertragungsverhältnis
Impedanz am Stromausgang (zwischen 0…12 Ω)
Impedanz am Spannungsausgang (mindestens 1 kΩ)
Dynamisches Verhalten (Messsystem)
Ausgang 1:
Bandbreite (-3dB Amplitude IPr zu Imeas) siehe Anmerkung 1*)
Bandbreite (-3dB Amplitude IPr zu Imeas) siehe Anmerkung 1*) (Hersteller)
Verzögerungszeit (Totzeit)
minimale Anstiegsgeschwindigkeit
minimale Anstiegsgeschwindigkeit (Hersteller)
Ausgang 2:
Bandbreite (-3dB)
Genauigkeit (des Messsystems)
Ausgang 1:
1) DC Offset bezogen auf den Strommessbereich
2) DC Ablesegenauigkeit (vom Messwert)
Gesamte DC Genauigkeit
3) Ausgangsrauschen (Spitze-Spitze) bezogen auf den Nennstrom
4) AC Amplitudenfehler (frequenzbezogene Genauigkeit)
Gesamte AC Genauigkeit
| Output 2 | Ausgang 2:
Zulässiger absoluter Fehler der DC Lupe / Ausgang 2
| Permissible absolute error of output 2 / DC loupe (Manufacturer) | Zulässiger absoluter Fehler der DC Lupe / Ausgang 2 (Hersteller)
Stromversorgung (Elektronikmodul)
Nennspannung; (Unipolar / Bipolar) / (110VDC oder 220VDC)
Spannungstoleranz, Minimum
Spannungstoleranz, Maximum
Schnittstellen Daten
Schnittstellen am Elektronikmodul
Schnittstelle am Messkopf
Erforderliche Länge der Verbindungskabel
Verbindungskabeltyp
Mechanische Daten
Maximal zulässige Kräfte an Primäranschlüssen, statisch
Maximal zulässige Kräfte an Primäranschlüssen, dynamisch
Vorortprüfung des Gasdichtewächtes ohne Demontage möglich
Projektspezifische Daten
Wartungsintervall
Maximale Umgebungstemperatur
| Quantities | Mengen
Hauptlieferung
benötigte Elektronikmodule
Ersatzteile
benötigte Elektronikmodule
| Head shorting plug (at Measuring Head) | Kurzschlussstecker (Messkopf) | nur für HITACC
| Short ciruit socket (for EM exchange) | Kurzschlussbuchse (für EM Tausch) | nur für HITACC
| Note 1*) IPr 100% Amplitude for 0…500 Hz; De-rate IPr inversely proportional to 5% at 10 kHz and higher | Notiz 1*) IPr 100% Amplitude f+r 0…500 Hz; Herabstufung von Ipr, umgekehrt proportional ab 5% bei 10 kHz und höher

## GA Bipole Overview
=== Confidential ==== for internal use only; please delete this tab before sending external
GA Bipole Overview:
Thermischer Bemessungskurzschlussstrom (Ith)
|  | DC Überlagerte Blitzstoßspannung | Leiter - Erde
Leiter - Erde
|  | DC Überlagerte Schaltstoßspannung | Leiter - Erde
Leiter - Erde
| Minimum creepage distance | Minimaler Kriechweg
Anforderungen an AC belastete (Innenraum- / Freiluftaufstellung) und DC belastete (Innenraum) Isolatorprofile (gemäß IEC 60815-2/3)
Nennstrom (1 p.u.) von Ausgang 1
Strommessbereich (2 p.u.) von Ausgang 1
Strommessbereich von Ausgang 2
Max. Überlaststrom
Keine Sättigung des Messkopfs
Type des Messkopfes
Anzahl der Messköpfe
Messsystem Daten
Elektronikmodul Typ
Ausgang 1: Übertragungsverhältnis
Ausgang 2: Übertragungsverhältnis
Impedanz am Stromausgang (zwischen 0…12 Ω)
Impedanz am Spannungsausgang (mindestens 1 kΩ)
Dynamisches Verhalten (Messsystem)
Ausgang 1:
Bandbreite (-3dB Amplitude IPr zu Imeas) siehe Anmerkung 1*)
Bandbreite (-3dB Amplitude IPr zu Imeas) siehe Anmerkung 1*) (Hersteller)
Verzögerungszeit (Totzeit)
minimale Anstiegsgeschwindigkeit
minimale Anstiegsgeschwindigkeit (Hersteller)
Ausgang 2:
Bandbreite (-3dB)
Genauigkeit (des Messsystems)
Ausgang 1:
1) DC Offset bezogen auf den Strommessbereich
2) DC Ablesegenauigkeit (vom Messwert)
Gesamte DC Genauigkeit
3) Ausgangsrauschen (Spitze-Spitze) bezogen auf den Nennstrom
4) AC Amplitudenfehler (frequenzbezogene Genauigkeit)
Gesamte AC Genauigkeit
| Output 2 | Ausgang 2:
Zulässiger absoluter Fehler der DC Lupe / Ausgang 2
| Permissible absolute error of output 2 / DC loupe (Manufacturer) | Zulässiger absoluter Fehler der DC Lupe / Ausgang 2 (Hersteller)
Stromversorgung (Elektronikmodul)
Nennspannung; (Unipolar / Bipolar) / (110VDC oder 220VDC)
Spannungstoleranz, Minimum
Spannungstoleranz, Maximum
Schnittstellen Daten
Schnittstellen am Elektronikmodul
Schnittstelle am Messkopf
Erforderliche Länge der Verbindungskabel
Verbindungskabeltyp
Mechanische Daten
Maximal zulässige Kräfte an Primäranschlüssen, statisch
Maximal zulässige Kräfte an Primäranschlüssen, dynamisch
Vorortprüfung des Gasdichtewächtes ohne Demontage möglich
Projektspezifische Daten
Wartungsintervall
Maximale Umgebungstemperatur
| Quantities | Mengen
Hauptlieferung
benötigte Elektronikmodule
Ersatzteile
benötigte Elektronikmodule
| Head shorting plug (at Measuring Head) | Kurzschlussstecker (Messkopf) | nur für HITACC
| Short ciruit socket (for EM exchange) | Kurzschlussbuchse (für EM Tausch) | nur für HITACC
| Note 1*) IPr 100% Amplitude for 0…500 Hz; De-rate IPr inversely proportional to 5% at 10 kHz and higher | Notiz 1*) IPr 100% Amplitude f+r 0…500 Hz; Herabstufung von Ipr, umgekehrt proportional ab 5% bei 10 kHz und höher

## Rigid Bipole Overview
=== Confidential ==== for internal use only; please delete this tab before sending external
Rigid Bipole Overview:

## Symm Monopole Overview
=== Confidential ==== for internal use only; please delete this tab before sending external
Symm Monopole Overview:

## Log_on
Datum | Name | Bemerkung | Rev.
2015-08-27 | A. Rodrigues | First issue | 0
2015-10-08 | A. Rodrigues | amneded test chapter (yellow part) | A
2016-03-03 | A. Rodrigues | ameded insulator descriptions | B
2017-03-16 | A. Rodrigues | amended SF6 Valve | C
2017-04-18 | A. Rodrigues | amended requirements towards to Customer and distinction half/full bridge converters | D
2017-07-12 | A. Rodrigues | references to source | E=5
2018-06-07 | A. Rodrigues | amended tab card for index guidline v8 | 6
2018-08-31 | U. Frank | Item "Insulation coordination…" added | 7
2019-07-24 | L. Hoppe | addition of information about type and quantity of required electronics modules for operation , modularisation number | 8
2019-10-28 | A. Rodrigues | Amended quantity description and separated voltage levels for AC and DC | 9
2019-11-21 | A. Rodrigues | Amended cells for Short Circuit Plug or Short Circuit Socket | 10
2021-02-01 | B. Plasser | Creepage factor | 11
2021-10-18 | M. Boslau | Spacing versus shed overhang | 12
2022-08-22 | B. Plasser | Update of purl links with aspectNames | 13