## Cover Sheet
BA111 / AC Current Transformers
Technical Data Sheet Template TC010
Technical Classification:
ECCN: | N | AL: | N |  | Angebotsdatum
These items are controlled by the U.S. Government (when labeled with “ECCN” unequal “N”) and authorized for export only to the country of ultimate destination for use by the ultimate consignee or end-user(s) herein identified. They may not be resold, transferred, or otherwise disposed of, to any other country or to any person other than the authorized ultimate consignee or end-user(s), either in their original form or after being incorporated into other items, without first obtaining approval from the U.S. Government or as otherwise authorized by U.S. law and regulations. Items labeled with "AL” unequal "N” are subject to European / national export authori-zation. Items without label or with label "AL:N" / "ECCN:N" or label”AL:9X9999” / “ECCN:9X9999”, may require authorization from responsible authorities depending on the final end-use, or the destination.
Restricted © Siemens Energy Global GmbH & Co. KG, 2021 Siemens Energy is a registered trademark licensed by Siemens AG.
Transmittal, reproduction, dissemination and/or editing of this document as well as utilization of its contents and communication thereof to others without express authorization are prohibited. Offenders will be held liable for payment of damages. All rights created by patent grant or Registration of a utility model or design patent are reserved.
Gerätetyp
Isolationspunkt entsprechend der Isolationskoordination
|  |  |  | Ausführungsart | (Innen / Außen)
|  |  |  | Isolationsmedium | (Öl / SF6 / Epoxidharz / Vakuum)
Typ des Isolators
Isolatorfarbe
|  |  |  | Lichtbogenschutzklasse IEC 61869-1, cl. 6.9 | (KlasseI oder Klasse II)
Oberflächenbehandlung
Elektrische Daten
|  |  |  | Bemessungsspannung Upr | (Leiter - Leiter)
Maximale Dauerbetriebsspannung AC (MCOV)
Nennfrequenz fr
Thermischer Bemessungskurzschlussstrom (Ith)
Kurzschlussdauer
|  |  |  | LIWV Blitzstoßspannungspegel | (Leiter - Erde)
Spannung zur Kriechwegsberechnung (BVCC)
Minimaler Kriechweg (Da < 300mm)
|  |  |  | Bemerkung: Durchmesser- korrektur gemäß General Data | spezifisch (Leiter gegen Erde)
absolut
Anforderungen an AC belastete (Innenraum- / Freiluftaufstellung) Isolatorprofile (gemäß IEC 60815-2/3)
|  |  |  | Kriechwegsfaktor CF (l/s) | Porzellan (non-HTM)
Verbundstoff / Hybrid (HTM)
Max. RIV Level bei 1.1*Um /Ö3

## Index of Revisions
Revision Index not for the supplier - Please delete before sending to supplier!
Index of Revisions of Template
Rev. | Date | Revisions | Author | Reviewer | Approver
16 | 2022-01-10 | New template, German translations, PAM links | B. Plasser |  | M. Boslau

## TC010_BA111
|  | 15 |  | Revisions
|  | Index |  | Remarks | Date |  | Remarks | Rev of EEC010 | Rev of Study
|  | 0 |  | First issue | 09.09.2024 | CG |  | 00 | Prepared on keeping the reference of Norfolk Vanguard West
2
3
4
5
|  | 6 | [5 empty] | `
7
Complete TD3 | only for ED3
| x | Doc. Ref.: |  | N-000261_TC_BA111_VGEO_EEC010 |  |  | Project name: Norfolk Vanguard East
| x | Doc. Title: |  | Technical Data Sheet, AC Voltage Transformer (VT)
x
x | x |  | English | Converter Stations |  |  | Norfolk Onshore Station
x |  |  |  | Location Designation acc. to SLD |  |  | #VGWO-CA10-Q01-BA01
x |  |  |  | Items |  | Units | VGWO_M_01
x |  |  |  | Modularisation Number | Basic Type
Type Description
x |  |  |  | Supplier | Offer number
x |  |  |  |  | Offer Item
x |  |  |  |  | Offer date
x | x | 1 |  | Main Data
x |  | 1.1 |  | Application |  |  | Network side
x | x | 1.2 |  | Type of device | (Capacitive / inductive) |  | inductive
x | x | 1.3 |  | Insulation Location according to Insulation Coordination |  |  | L
x | x | 1.4 |  | Installation location | (indoor / outdoor) |  | outdoor
x | x | 1.5 |  | Type of insulation | (oil / SF6 / epoxy resin / clean air) |  | SF6
x | x | 1.6 |  | Type of insulator | (composite / porcelain / epoxy resin) |  | Composite
x |  | 1.7 |  | Color of insulator |  |  | refer to General Data
x |  | 1.8 |  | Internal arc protection class IEC 61869-1, cl. 6.9 | (class I or class II) |  | to be specified by supplier
x |  | 1.9 |  | Surface treatment |  |  | Refer to General Data
x | x | 2 |  | Electrical data
x | x | 2.1 |  | Rated primary voltage | (ph - ph) | kV | 400
x | x | 2.2 |  | MCOV (Maximum Continuous Operating Voltage) (ph - ph) |  | kV | 420
x | x | 2.3 |  | Rated frequency fr |  | Hz | 50
x |  | 2.4 |  | Rated short-time thermal current (Ith) |  | kA | 63
x |  | 2.5 |  | Short-time duration |  | s | 1
x | x | 2.6 |  | LIWV (Lightning impulse withstand voltage) |  | kVpeak | 1425
x | x | 2.7 |  | SIWV (Switching impulse withstand voltage) |  | kVpeak | 1050
x | x | 2.8 |  | Base voltage for creepage calculation | (ph - gnd) | kV | 242.5*)
x | x | 2.9 |  | Minimum creepage distance (Da < 300mm)
x | x | 2.10 |  | Note: Diameter correction acc. to General Data | specific (ph - gnd) | mm/kV | 53.6936
x | x | 2.11 |  |  | total (ph - gnd) | mm | 13022
x |  | 2.15 |  | Requirements for AC Voltage Indoor/Outdoor Insulator Shed Profiles (as per IEC 60815-2/3)
x |  | 2.16 |  | Creepage factor CF (l/s) | Porcelain (non-HTM) |  | <3.5
x |  | 2.17 |  |  | Composite / Hybrid (HTM) |  | <4.2
x | x | 2.18 |  | Max. RIV level at 1.1*Um / √3 | (line to ground) | µV | 2500
x | x | 2.19 |  | Rated voltage factor | (continuous) | % | 1.2
x | x | 2.20 |  |  | (for 30 seconds) | % | 1.4
x |  | 2.21 |  | Active ferroresonance-suppression circuits |  | yes or no | 1.5
x |  | 2.22 |  | Protection of second. winding, in term. box (MCB / fuse) |  |  | yes
x |  | 2.23 |  | Overvoltage protection device (spark gap or similar) |  |  | MCB
x | x | 3 |  | Core (Winding) data
x | x | 3.1 |  | Winding no.
x | x | 3.2 |  | Accuracy class |  |  | 0.5/3P
x | x | 3.3 |  | Rated transformation ratio kr (line to ground) |  | kV // V | 396/√3 : 110/√3
x | x | 3.4 |  | Rated burden |  | VA | 50
x | x | 3.5 |  | Winding no. 2
x | x | 3.6 |  | Accuracy class |  |  | 0.5/3P
x | x | 3.7 |  | Rated transformation ratio kr (line to ground) |  | kV // V | 396/√3 : 110/√3
x | x | 3.8 |  | Rated burden |  | VA | 50
x | x | 3.9 |  | Winding no. 3
x | x | 3.10 |  | Accuracy class |  |  | 0.2
x | x | 3.11 |  | Rated transformation ratio kr (line to ground) |  | kV // V | 396/√3 : 110/√3
x | x | 3.12 |  | Rated burden |  | VA | 15
x | x | 4 |  | Mechanical data
x | x | 4.1 |  | Terminal forces, static |  | kN | 2
x | x | 4.2 |  | Terminal forces, dynamic |  | kN | 5
x | x | 4.3 |  | On-site testing of the gas-density meter without deinstallation (e.g.WIKA Valve Testing Device) |  |  | Yes
x |  | 5 |  | Project related data
x |  | 5.1 |  | Minimum ambient temperature |  | °C | -10
x |  | 5.2 |  | Maximum ambient temperature |  | °C | +35
x | x | 6 |  | quantity
x | x | 6.1 |  | main (1-ph units) |  | pcs | 3
x | x | 6.2 |  | spares (1-ph units) |  | pcs | 1
x
x |  | Part of subcontractor - please fill in in the yellow marked cells
x |  | Rev |  | Remarks | Date |  | Remarks | Date | by | Norfolk Onshore Station | #REF! | #REF!
x |  | 0 | [7 empty] | #VGWO-CA10-Q01-BA01 | #REF! | #REF!
x |  | 1 | [7 empty] | VGWO_M_01 | #REF! | #REF!
x |  | 2
x |  | 3
x
x | [9 empty] | please fill in the yellow marked cells | please fill in the yellow marked cells
x |  |  |  | Part for subcontractor |  |  | Part for subcontractor
x |  |  |  | - please fill out - |  |  | - please fill out - |  |  | offered | offered | offered
x |  | 1 |  | Manufacturer type identification |  |  | Manufacturer type identification
x |  | 1.1 |  | Manufacturer |  |  | Manufacturer |  |  | Trench Germany
x |  | 1.2 |  | Type |  |  | Type |  |  | SVS420
x |  | 2 |  | Main Data |  |  | Main Data
x |  | 2.1 |  | Insulation medium (SF6 / oil / epoxy resin |  |  | Insulation medium (SF6 / oil / epoxy resin |  |  | SF6
x |  | 2.2 |  | Gas(es) for final filling included ? | (Yes/No) |  | Gas(es) for final filling included ? | (Yes/No) |  | NO
x |  | 2.3 |  | Insulator type (porcelain / composite / epoxy resin) |  |  | Insulator type (porcelain / composite / epoxy resin) |  |  | composite
x |  | 2.4 |  | Type of device | (Capacitve/inductive) |  | Type of device | (Capacitve/inductive) |  | inductive
x |  | 2.5 |  | Place of installation | (outdoor/indoor) |  | Place of installation | (outdoor/indoor) |  | outdoor
x |  | 3 |  | Reliability, Availability, Maintainability |  |  | Reliability, Availability, Maintainability
x |  | 3.1 |  | MTBF or MTTF |  |  | MTBF or MTTF |  | h
x |  | 3.2 |  | tcorr (Fault correction or restoration time) | incl. time required for related work on the concerned component or on neighbouring equipment |  | tcorr (Fault correction or restoration time) | incl. time required for related work on the concerned component or on neighbouring equipment | h | Note for suppliers: By this indication an average downtime / repairing time will be calculated, which doesn´t figure a guaranteed time. This value will not be fixed in the contract, it should be a quite good estimated value. (under the assumption, necessary tools and lifting ramps etc. are locally available) | Note for suppliers: By this indication an average downtime / repairing time will be calculated, which doesn´t figure a guaranteed time. This value will not be fixed in the contract, it should be a quite good estimated value. (under the assumption, necessary tools and lifting ramps etc. are locally available) | Note for suppliers: By this indication an average downtime / repairing time will be calculated, which doesn´t figure a guaranteed time. This value will not be fixed in the contract, it should be a quite good estimated value. (under the assumption, necessary tools and lifting ramps etc. are locally available)
x |  | 3.3 |  | ttest (Time for adjustment, setting, checking and testing of repaired or replaced equipment) |  |  | ttest (Time for adjustment, setting, checking and testing of repaired or replaced equipment) |  | h
x |  | 4 |  | Electrical data |  |  | Electrical data
x |  | 4.1 |  | Rated primary voltage | (Line to line) |  | Rated primary voltage | (Line to line) | kV | 420
x |  | 4.2 |  | MCOV (Maximum Continuous Operating voltage) (ph - ph) |  |  | MCOV (Maximum Continuous Operating voltage) (ph - ph) |  | kV AC | 440
x |  | 4.3 |  | Absolute creepage distance |  |  | Absolute creepage distance |  | mm | 13020
x |  | 4.4 |  | LIWV (Lightning impulse withstand voltage) |  |  | LIWV (Lightning impulse withstand voltage) |  | kVpeak | 1425
x |  | 4.5 |  | SIWV (Switching withstand voltage) |  |  | SIWV (Switching withstand voltage) |  | kVpeak | 1050
x |  | 4.6 |  | PFWV (Power frequency withstand voltage |  |  | PFWV (Power frequency withstand voltage |  | kVrms | 680
x |  | 4.7 |  | Rated voltage factor | (continuous) |  | Rated voltage factor | (continuous) | p.u. | 1.2
x |  | 4.8 |  | Rated voltage factor | (for 30 seconds) |  | Rated voltage factor | (for 30 seconds) | p.u. | 1,5/30s
x |  | 4.9 |  | Rated short-time thermal current (Ith) |  |  | Rated short-time thermal current (Ith) |  | kA | 63
x |  | 4.10 |  | duration |  |  | duration |  | s | 1
x |  | 4.11 |  | Active ferroresonance-suppression circuits (YES / NO) |  |  | Active ferroresonance-suppression circuits (YES / NO) |  |  | air gap in magnetic core
x |  | 4.12 |  | Protection of second. winding, in term. box (MCB / fuse) |  |  | Protection of second. winding, in term. box (MCB / fuse) |  |  | yes
x |  | 4.13 |  | Overvoltage protection device (spark gap or equal) |  |  | Overvoltage protection device (spark gap or equal) |  |  | no
x |  | 5 |  | Insulator |  |  | Insulator
x |  | 5.1 |  | Type of insulator | (composite / porcelain / epoxy resin) |  | Type of insulator | (composite / porcelain / epoxy resin) |  | composite
x |  | 5.2 |  | Average diameter Da of insulator |  |  | Average diameter Da of insulator |  | mm | 455.5
x |  | 5.3 |  | Shafted insulator |  |  | Shafted insulator |  | yes/no | no
x |  | 5.4 |  | Colour of insulator |  |  | Colour of insulator |  |  | grey
x |  | 5.5 |  | Min. mechanical bending load |  |  | Min. mechanical bending load |  | kN | 2
x |  | 5.6 |  | Shed profile |  |  | Shed profile |  | -
x |  | 5.7 |  | Shed extension | (long / short) |  | Shed extension | (long / short) | mm | 50/35
x |  | 5.8 |  | Shed spacing between long sheds | (> 69) |  | Shed spacing between long sheds | (> 69) | mm | 50
x |  | 5.9 |  | Manufacturer of insulator |  |  | Manufacturer of insulator
x |  | 5.10 |  | Type of silicone material | (RTV/LSR/HTV) |  | Type of silicone material | (RTV/LSR/HTV) |  | LSR
x |  | 5.11 |  | Type test protokoll | (yes / no / report / no) |  | Type test protokoll | (yes / no / report / no) |  | no
x |  | 5.12 |  | Drawing of insulator |  |  | Drawing of insulator
x |  | 5.13 |  | RTV coating | yes/no |  | RTV coating | yes/no |  | no
x |  | 5.14 |  | Creepage factor (C.F.) |  |  | Creepage factor (C.F.) |  | - | 3.807
x |  | 5.15 |  | Minimum arcing distance | terminal - ground |  | Minimum arcing distance | terminal - ground | mm | 3420
x |  | 6 |  | Mechanical data |  |  | Mechanical data
x |  | 6.1 |  | Total weight of device |  |  | Total weight of device |  | kg | 1274
x |  | 6.2 |  | Total Height |  |  | Total Height |  | mm | 4798
x |  | 6.3 |  | Total Width |  |  | Total Width |  | mm | 1304
x |  | 6.4 |  | Total Depth |  |  | Total Depth |  | mm | 1304
x |  | 6.5 |  | Mechanical terminal load in all direction |  |  | Mechanical terminal load in all direction
x |  | 6.6 |  |  | Static |  |  | Static | kN | 2
x |  | 6.7 |  |  | Dynamic |  |  | Dynamic | kN | 5
x |  | 6.8 |  | Terminal Standard (IEC, NEMA,...) | HV |  | Terminal Standard (IEC, NEMA,...) | HV |  | Norm F1, F2 … | Norm F1, F2 …
x |  | 6.9 |  | (terminal blocks, ..) | LV |  | (terminal blocks, ..) | LV |  | Norm F1, F2 … | Norm F1, F2 …
x |  | 6.10 |  | (IEC, NEMA, terminal blocks...) | Gr |  | (IEC, NEMA, terminal blocks...) | Gr |  | Norm F1, F2 … | Norm F1, F2 …
x |  | 6.11 |  | Ambient air temperature range |  |  | Ambient air temperature range
x |  | 6.12 |  |  | min. |  |  | min. | °C | 40
x |  | 6.13 |  |  | max. |  |  | max. | °C | -30
x |  | 6.14 |  | Altitude above sea level |  |  | Altitude above sea level |  | m | 1000
x |  | 6.15 |  | Wind velocity |  |  | Wind velocity |  | m/s | 34
x |  | 6.16 |  | Ice coating |  |  | Ice coating |  | mm | 20
x |  | 6.17 |  | Acceleration in centre of gravity |  |  | Acceleration in centre of gravity
x |  | 6.18 |  |  | horizontal |  |  | horizontal | g | 0.1
x |  | 6.19 |  |  | vertical |  |  | vertical | g | 0.1
x |  | 7 |  | Core (Winding) data |  |  | Core (Winding) data |  |  | Confirmed as per Winding spec
x |  | 7.1 |  | Winding no. 1 |  |  | Winding no. 1
x |  | 7.2 |  | Class |  |  | Class
x |  | 7.3 |  | Accuracy Rating Voltages (line to ground) |  |  | Accuracy Rating Voltages (line to ground) |  | kV // V
x |  | 7.4 |  | Rated burden |  |  | Rated burden |  | VA
x |  | 7.5 |  | Thermal continuous secondary current | Ith |  | Thermal continuous secondary current | Ith | A
x |  | 7.6 |  | Winding no. 2 |  |  | Winding no. 2
x |  | 7.7 |  | Class |  |  | Class
x |  | 7.8 |  | Accuracy Rating Voltages (line to ground) |  |  | Accuracy Rating Voltages (line to ground) |  | kV // V
x |  | 7.9 |  | Rated burden |  |  | Rated burden |  | VA
x |  | 7.10 |  | Thermal continuous secondary current | Ith |  | Thermal continuous secondary current | Ith | A
x |  | 7.11 |  | Winding no. 3 |  |  | Winding no. 3
x |  | 7.12 |  | Class |  |  | Class
x |  | 7.13 |  | Accuracy Rating Voltages (line to ground) |  |  | Accuracy Rating Voltages (line to ground) |  | kV // V
x |  | 7.14 |  | Rated burden |  |  | Rated burden |  | VA
x |  | 7.15 |  | Thermal continuous secondary current | Ith |  | Thermal continuous secondary current | Ith | A
x |  | 8 |  | Type Test IVT* | Standard |  | Type Test IVT* | Standard
x |  | 8.1 |  | Temperature rise test | IEC 61869-3 cl. 7.2.2 |  | Temperature rise test | IEC 61869-3 cl. 7.2.2 | EUR | 37000
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | yes
x |  | 8.2 |  | Impulse voltage withstand test on primary terminals | IEC 61869-3 cl. 7.2.3 |  | Impulse voltage withstand test on primary terminals | IEC 61869-3 cl. 7.2.3 | - | - | - | -
x |  |  |  | Lightning impulse voltage test on primary terminals | IEC 61869-3, cl. 7.2.3.2 |  | Lightning impulse voltage test on primary terminals | IEC 61869-3, cl. 7.2.3.2 | EUR | Sequence of nine waves (full/chopped) is free of charge (total 9 waves) and planned together with routine tests. If full sequence is required cost is 4400€.
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | yes
x |  |  |  | Switching impulse voltage test | IEC 61869-3, cl. 7.2.3.3 |  | Switching impulse voltage test | IEC 61869-3, cl. 7.2.3.3 | EUR | 4400
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | yes
x |  | 8.3 |  | Wet test for outdoor type transformers | IEC 61869-3 cl. 7.2.4 |  | Wet test for outdoor type transformers | IEC 61869-3 cl. 7.2.4 | EUR | 8000
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | yes
x |  | 8.4 |  | Electromagnetic Compatibility tests | IEC 61869-3 cl. 7.2.5 |  | Electromagnetic Compatibility tests | IEC 61869-3 cl. 7.2.5 | EUR | 2500
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | yes
x |  | 8.5 |  | Test for accuracy | IEC 61869-3 cl. 7.2.6 |  | Test for accuracy | IEC 61869-3 cl. 7.2.6 | EUR | free of charge
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | routine test
x |  | 8.6 |  | Verification of the degree of protection by enclosures | IEC 61869-3 cl. 7.2.7 |  | Verification of the degree of protection by enclosures | IEC 61869-3 cl. 7.2.7 | EUR | 8000
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | yes
x |  | 8.7 |  | Enclosure tightness test at ambient temperature | IEC 61869-3 cl. 7.2.8 |  | Enclosure tightness test at ambient temperature | IEC 61869-3 cl. 7.2.8 | EUR | free of charge
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | routine test
x |  | 8.8 |  | Pressure test for the enclosure | IEC 61869-3 cl. 7.2.9 |  | Pressure test for the enclosure | IEC 61869-3 cl. 7.2.9 | EUR | pressure test are available for the subcomponents from manufacturers after manufacturing
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | Report/s can be provided upon request
x |  | 8.9 |  | Short -circuit withstand capability test | IEC 61869-3 cl. 7.2.301 |  | Short -circuit withstand capability test | IEC 61869-3 cl. 7.2.301 | EUR | 8000
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | yes
x |  | 9 |  | Type Test CVT* | Standard |  | Type Test CVT* | Standard
x |  | 9.1 |  | Temperature rise test | IEC 61869-5 cl. 7.2.2 |  | Temperature rise test | IEC 61869-5 cl. 7.2.2 | EUR | na
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | na
x |  | 9.2 |  | Chopped impulse test | IEC 61869-5 cl.7.4.1 |  | Chopped impulse test | IEC 61869-5 cl.7.4.1 | EUR | na
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | na
x |  | 9.3 |  | Impulse voltage withstand test on primary terminals | IEC 61869-5 cl. 7.2.3 |  | Impulse voltage withstand test on primary terminals | IEC 61869-5 cl. 7.2.3 | - | na | - | -
x |  |  |  | Lightning impulse voltage test on primary terminals | IEC 61869-5, cl. 7.2.3.2 |  | Lightning impulse voltage test on primary terminals | IEC 61869-5, cl. 7.2.3.2 | EUR | na
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | na
x |  |  |  | Switching impulse voltage test | IEC 61869-5, cl. 7.2.3.3 |  | Switching impulse voltage test | IEC 61869-5, cl. 7.2.3.3 | EUR | na
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | na
x |  | 9.4 |  | Wet test for outdoor type transformers | IEC 61869-5 cl. 7.2.4 |  | Wet test for outdoor type transformers | IEC 61869-5 cl. 7.2.4 | EUR | na
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | na
x |  | 9.5 |  | Electromagnetic Compatibility tests | IEC 61869-5 cl. 7.2.5 |  | Electromagnetic Compatibility tests | IEC 61869-5 cl. 7.2.5 | EUR | na
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | na
x |  | 9.6 |  | Test for accuracy | IEC 61869-5 cl. 7.2.6 |  | Test for accuracy | IEC 61869-5 cl. 7.2.6 | EUR | na
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | na
x |  | 9.7 |  | Verification of the degree of protection by enclosures | IEC 61869-5 cl. 7.2.7 |  | Verification of the degree of protection by enclosures | IEC 61869-5 cl. 7.2.7 | EUR | na
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | na
x |  | 9.8 |  | Enclosure tightness test at ambient temperature | IEC 61869-5 cl. 7.2.8 |  | Enclosure tightness test at ambient temperature | IEC 61869-5 cl. 7.2.8 | EUR | na
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | na
x |  | 9.9 |  | Pressure test for the enclosure | IEC 61869-5 cl. 7.2.9 |  | Pressure test for the enclosure | IEC 61869-5 cl. 7.2.9 | EUR | na
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | na
x |  | 9.10 |  | Capacitance and tan δ measurement at power frequency | IEC 61869-5 cl.7.2.501 |  | Capacitance and tan δ measurement at power frequency | IEC 61869-5 cl.7.2.501 | EUR | na
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | na
x |  | 9.11 |  | Short -circuit withstand capability test | IEC 61869-5 cl. 7.2.502 |  | Short -circuit withstand capability test | IEC 61869-5 cl. 7.2.502 | EUR | na
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | na
x |  | 9.12 |  | Ferro-resonance test | IEC 61869-5 cl. 7.2.503 |  | Ferro-resonance test | IEC 61869-5 cl. 7.2.503 | EUR | na
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | na
x |  | 9.13 |  | Transient response test (for protective capacitive transformers) | IEC 61869-5 cl. 7.2.504 |  | Transient response test (for protective capacitive transformers) | IEC 61869-5 cl. 7.2.504 | EUR | na
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | na
x |  | 9.14 |  | Type test for carrier frequency accessories | IEC 61869-5 cl. 7.2.505 |  | Type test for carrier frequency accessories | IEC 61869-5 cl. 7.2.505 | EUR | na
x |  |  |  |  | existing report available? |  |  | existing report available? | yes/no | na
x |  |  |  | *Existing reports of equipment with identical design and similar rating can also be accepted, if evidence of applicability can be provided |  |  | *Existing reports of equipment with identical design and similar rating can also be accepted, if evidence of applicability can be provided
x |  | 10 |  | Routine Test IVT | Standard |  | Routine Test IVT | Standard | included
x |  | 10.1 |  | Power-frequency withstand tests on primary terminals | IEC 61869-3 cl. 7.3.1 |  | Power-frequency withstand tests on primary terminals | IEC 61869-3 cl. 7.3.1 | yes/no | yes
x |  | 10.2 |  | Partial discharge measurement | IEC 61869-3 cl. 7.3.2 |  | Partial discharge measurement | IEC 61869-3 cl. 7.3.2 | yes/no | yes
x |  | 10.3 |  | Power-frequency withstand tests between sections | IEC 61869-3 cl. 7.3.3 |  | Power-frequency withstand tests between sections | IEC 61869-3 cl. 7.3.3 | yes/no | yes
x |  | 10.4 |  | Power-frequency withstand tests on secondary terminals | IEC 61869-3 cl. 7.3.4 |  | Power-frequency withstand tests on secondary terminals | IEC 61869-3 cl. 7.3.4 | yes/no | yes
x |  | 10.5 |  | Test for accuracy | IEC 61869-3 cl. 7.3.5 |  | Test for accuracy | IEC 61869-3 cl. 7.3.5 | yes/no | yes
x |  | 10.6 |  | Verification of terminal markings | IEC 61869-3 cl. 7.3.6 |  | Verification of terminal markings | IEC 61869-3 cl. 7.3.6 | yes/no | yes
x |  | 10.7 |  | Enclosure tightness test at ambient temperature | IEC 61869-3 cl. 7.3.7 |  | Enclosure tightness test at ambient temperature | IEC 61869-3 cl. 7.3.7 | yes/no | yes
x |  | 10.8 |  | Pressure test for the enclosure | IEC 61869-3 cl. 7.3.8 |  | Pressure test for the enclosure | IEC 61869-3 cl. 7.3.8 | yes/no | yes, made by manufacturer od single paer
x |  | 11 |  | Routine Test CVT | Standard |  | Routine Test CVT | Standard | included
x |  | 11.1 |  | Power-frequency withstand tests on primary terminals | IEC 61869-5 cl. 7.3.1 |  | Power-frequency withstand tests on primary terminals | IEC 61869-5 cl. 7.3.1 | yes/no | na
x |  | 11.2 |  | Partial discharge measurement | IEC 61869-5 cl. 7.3.2 |  | Partial discharge measurement | IEC 61869-5 cl. 7.3.2 | yes/no | na
x |  | 11.3 |  | Power-frequency withstand tests between sections | IEC 61869-5 cl. 7.3.3 |  | Power-frequency withstand tests between sections | IEC 61869-5 cl. 7.3.3 | yes/no | na
x |  | 11.4 |  | Power-frequency withstand tests on secondary terminals | IEC 61869-5 cl. 7.3.4 |  | Power-frequency withstand tests on secondary terminals | IEC 61869-5 cl. 7.3.4 | yes/no | na
x |  | 11.5 |  | Test for accuracy | IEC 61869-5 cl. 7.3.5 |  | Test for accuracy | IEC 61869-5 cl. 7.3.5 | yes/no | na
x |  | 11.6 |  | Verification of terminal markings | IEC 61869-5 cl. 7.3.6 |  | Verification of terminal markings | IEC 61869-5 cl. 7.3.6 | yes/no | na
x |  | 11.7 |  | Enclosure tightness test at ambient temperature | IEC 61869-5 cl. 7.3.7 |  | Enclosure tightness test at ambient temperature | IEC 61869-5 cl. 7.3.7 | yes/no | na
x |  | 11.8 |  | Pressure test for the enclosure | IEC 61869-5 cl. 7.3.8 |  | Pressure test for the enclosure | IEC 61869-5 cl. 7.3.8 | yes/no | na
x |  | 11.9 |  | Ferro-resonance check | IEC 61869-5 cl. 7.3.501 |  | Ferro-resonance check | IEC 61869-5 cl. 7.3.501 | yes/no | na
x |  | 11.10 |  | Routine test for carrier frequency accessories | IEC 61869-5 cl. 7.3.502 |  | Routine test for carrier frequency accessories | IEC 61869-5 cl. 7.3.502 | yes/no | na

## TC_Revision_Index_Guideline
TC Revision Index Guideline
Introduction to Guideline
This description shall be a guideline for EE and suppliers revising TC’s and assigning a practical revision numeration correctly. Problem is, that SAG and supplier use two different revision numberings for TC’s. A standard procedure guideline for revision numerating is given in this description, so that it will be easy understandable and applicable for both sides.
TC Revision Index Guideline
TC has three revision indices to manage: Rev of TC: This revision is enumerating the latest revised versions of the TC’s generated by EE. Rev of EC: This list is pursued with one higher index for each new EC version (sent to customer). Rev of Supplier: The supplier of the component has to increase the index by one for each of his new revision of the TC.
SAG-EE’s “Revision of the TC” index
An example for the top revision index list in the TC is shown in the Table 1 below. This top revision index list is designated to be filled in by SAG-EE. The TC revision index list enumeration is 0, 1, 2, ... and the correspondent TC file name P-xxxxxx_TC_AANNN_AANN_EEC010_2_S2. When the first TC version is established, the Rev of TC will be ‘0’, all by EE filled out fields shall have a white background colour (white part) and this TC is sent to supplier. The latest changes in the following TC’s, which are communicated for the first time to the supplier, have to be marked in yellow colour. Thereby, the new revision index lines and the regarding updated cells in the TC are meant. From Siemens Equipment Engineering, it is required, that updated TC’s are sent to the supplier with a higher revision index number immediately after completion. If the supplier gave information in the TC already and the component specification changed in a few points, supplier filled out cells should be kept in the latest TC document. When the component specification changes completely and a new offer is requested from the supplier, a TC with an empty and yellow marked supplier part should be given to supplier for quotation. In the right column next to the rightmost TC component specification column, information for the supplier might be offered from the EE with comments. By supplier missing or for revision required values should be highlighted with red coloured comments in this comment column.
P-xxxxxx_TC_AANNN_AANN_EEC010_3_S2_commented
Revisions
Rev of TC | Remarks | Date | by | Rev of EC
0 | First Issue | 2016-01-14 | AF | 00
1 | Wording in line 1.3 to 1.6 changed | 2016-01-29 | AF | -
2 | Changes acc. to agreement with System Design | 2016-02-26 | AF | 01
3 | Update acc. to Customer comments | 2016-04-19 | AF | 02
Table 1: Top revision index “Rev of TC” for the document P-xxxxxx_TC_AANNN_AANN_EEC010_3_S2_commented |  |  |  |  | Konverterstationen
Anlagenortskennzeichen nach SLD
TC’s “Rev of Supplier” Index |  |  |  |  | Gerät
The bottom “Rev of Supplier” index list in the light yellow part of TC is designated to be filled in by the suppliers. Supplier revision index numeration is S0, S1, S2, ... . S stands for supplier. So the supplier will also have a revision index list. To the TC excel file name, this index is appended as well after EE revision index, i.e. as P-xxxxxx_TC_AANNN_AANN_EEC010_2_S2_commented. The supplier has to fill out the revision index list with information about the latest changes. The manufacturer also marks changes clearly in TC for example by marking cells with yellow colour. Table 2 shows the bottom “Rev of Supplier” list, which is filled out by the supplier:
P-xxxxxx_TC_AANNN_AANN_EEC010_4_S2_commented
Rev of Supplier | Remarks | Date | by
S0 | First Design | 2016-01-28 | DU
S1 | Update acc. Rev 3 of TC / Rev B of EC | 2016-04-29 | DU
S2 | Update acc. Comments from EE | 2016-05-09 | DU
Type of device
Table 2: Supplier revision index “Rev of TC” for the document P-xxxxxx_TC_AANNN_AANN_EEC010_4_S2_commented
Typical and Possible TC revisions as example
The following Table 3 shows a typical history of TC document names; the revisions inside the document have to be the same:
TC document name
P-xxxxxx_TC_AANNN_AANN_EEC010_0
P-xxxxxx_TC_AANNN_AANN_EEC010_0_S0
P-xxxxxx_TC_AANNN_AANN_EEC010_0_S0_commented
P-xxxxxx_TC_AANNN_AANN_EEC010_0_S1
P-xxxxxx_TC_AANNN_AANN_EEC010_0_S1_commented
P-xxxxxx_TC_AANNN_AANN_EEC010_0_S2
P-xxxxxx_TC_AANNN_AANN_EEC010_1_S2_commented
P-xxxxxx_TC_AANNN_AANN_EEC010_1_S3
P-xxxxxx_TC_AANNN_AANN_EEC010_1_S3_commented
P-xxxxxx_TC_AANNN_AANN_EEC010_1_S4
P-xxxxxx_TC_AANNN_AANN_EEC010_1_S4_final
Table 3: TC document name history
[6 empty] | 0 | 13020 | 13020
Prevention of TC update conflicts between EE and suppliers
When a TC update is being sent to the supplier, it could arise that the TC is updated by the supplier parallel to current working from EE on the latest TC version. For that reason it is very important to act according to "the ball is in your court" principle. This means via communication it has to be clear who (EE or Supplier) is working on the TC. Parallel actions have to be avoided.

## Log_on
Datum | Name | Bemerkung | Rev.
2016-09-05 | Lars Bock | First issue | 0
2016-10-17 | Lars Bock | Revisions | 1
2016-10-27 | Lars Bock | Revisions | 2
2016-12-12 | Lars Bock | Revisions | 3
2016-12-13 | M.Boslau | Remarks M. Boslau | 4
2016-12-23 | Lars Bock | Revisions | 5
2017-01-20 | Lars Bock | Revisions | 6
2017-02-09 | Lars Bock | Revisions | 7
2017-03-09 | Lars Bock | Revisions | 8
2017-07-06 | Uwe Frank | Diverse Änderungen | 9
2018-06-07 | A. Rodrigues | amended register tab for index guideline v8 | 10
2018-06-26 | U. Frank | Changes to new IEC | 11
2018-09-05 | U. Frank | row "1.3 Insulation Location according to Insulation Coordination" added | 12
2019-01-29 | M.Boslau | Tests updated | 13
2019-02-06 | M. Boslau | Modularisation Block updated | 14
2021-02-01 | B. Plasser | Creepage factor and harmonic measurement tap added | 15
Konverterstationen
Anlagenortskennzeichen nach SLD
Gerät
Type of device
[5 empty] | 0 | 13020 | 13020